BEXHILL TO HASTINGS LINK ROAD

REVIEW OF CONTRACTORS DELIVERABLES

Drawing/Document reviewed:	Approval in Principle for S01 Chapel Path Underpass

Document Reference:		JB-B1297000-PH2/1600.06a/0001 (rev 0)

Date of Receipt:			10 September 2012

Date of Review by TAA:		12 September 2012

Date of Review Response:

The Drawings/Documents have been reviewed. The submission is NOT accepted.

The following comments below have been identified.  Please review all comments above, revise the drawings/document as appropriate, and provide a response to comments.

| AIP | Review Comment | Contractor’s Response |
| --- | --- | --- |
| Cl 4.1.1 Cl 4.1.2 Cl 4.1.3 | Reinstate BD 37/01 (as in original AIP), and retain BD 31/01. (BD 37/01 needs to be used in conjunction with BD 31/01, it is not replaced by BD 31/01) |  |
| Cl 4.1.2 | Original AIP stated 45units of HB loading, ( see emails dated 1 Sept 2009 between Jacobs, ESCC & Mott McDonald) |  |
| Cl 4.3 | The original AIP included two Departures from Standard, re CHE Memo 227/08 & IAN 96, (these had been agreed in advance and clarified that a sand asphalt layer was not normally required, and impregnation was also not required for BHLR structures. Please reinstate these as it clarifies what is proposed. |  |
| Cl 6.3 | Include that 20mm differential movement between the box structure and the approach embankments will be taken into account, and that provision will be made for this vertical movement for the safety barriers and the environmental barriers. |  |
| Cl 8.1 | Is the Drawing No. correct? (ie should it contain ‘06a’ rather than ‘01a’) Include Appendix E |  |
| Cl 10 | Please leave a space for any required Conditions/Amendments by TAA. |  |
| Appendix A TAS | Implementation BDs for BS 5400 are incorrect , (ie ‘See BD1’,etc) Reinstate BD 63/07 |  |
| Appendix B | Cover Sheet: Incorrect Drawing No? ( ie -01a-) |  |
| Appendix E | Is the statement that 2.5m wide verges are provided along the scheme mainline correct? For example the verges at S07 U/B are 1.2m both on and off the structure. |  |
| GA Drg | Drawing Number & Title on the drawing is not consistent with that stated on Appendix B Cover Sheet. Please add a note that water level in existing culvert will be investigated and that if required a flap valve will be provided at the discharge pipe from the underpass to prevent flooding in the underpass at times of high flow in the existing culvert. Does existing culvert surcharge? |  |